Pre-insulated HDPE-Jacketed Steel Piping Systems suitable for Steam, Condensate Return,
 and High Temperature Heating Water (Maximum operating Temperature of 366F).

##### Part 1 - General

1.1	Pre-insulated Piping Manufacturer shall furnish a complete HDPE jacketed system of factory pre-insulated steel piping for the specified service.  The jacket throughout the entire system shall incorporate electric fusion, butt fusion, or extrusion welding at all fittings, joint closures, or other points of connection.  This shall create a jacket that is seamless throughout the entire system with the exception of anchors, whose water shed rings are sealed with a double wrap heat shrink material prohibiting the ingression of water.  All pre-insulated pipe, fittings, insulating materials, and technical support shall be provided by the Pre-insulated Piping System manufacturer. Manufacturer shall provide a standard 1 year manufacturer’s warranty, which shall be extended to a 3 year warranty contingent on the leak detection system being monitored by the system owner.

1.2	A complete layout of the system, showing anchors, expansion provisions, and building entrance details, shall be provided by the pre-insulated pipe manufacturer.  Means for expansion must be made in pipe off-sets or loops.

1.3	The system shall be termed a high temperature foam system, with water spread limiting devices capable of preventing the deterioration of foam and spread of groundwater located at each individual factory piece, a resistance based leak detection monitoring system in the foam, and thermally isolated anchors as described herein.

Part 2 - Products

2.1	Carrier pipe shall be steel ASTM A-53, Grade B., ERW (Type E), standard weight for sizes 2” and larger, and shall be ASTM A-106, Grade B, standard weight for sizes 1-1/2” and smaller (Std. Wt. is the same as Sch. 40 through 10”).  Condensate return piping shall be extra strong (XS is the same as Sch. 80 through 8”).  When practical, piping shall be provided in 40-foot random lengths.  All carbon steel pipe shall have ends cut square and beveled for butt-welding.  Straight sections of factory insulated pipe shall have 6” of exposed pipe at each end for field joint fabrication.

2.2	Insulation shall be polyisocyanurate foam insulation bonded to both the jacketing and carrier pipe and either spray applied or high pressure injected with one shot into the annular space between carrier pipe and jacket with a nominal thickness of 2-1/2” for systems operating below 366°F.  Insulation shall be rigid, 85% closed cell foam insulation with not less than 2.4 pounds per cubic foot density, having a compressive strength of not less than 30 psi @ 75°F and a coefficient of thermal conductivity (K-Factor) not higher than 0.17 @ 75°F.  Maximum operating temperature of the system shall not exceed 366°F.

2.3   Water Stops (water spread limiting devices) shall be provided at each spool piece and length of pipe. A steel disk shall be welded to the carrier pipe and extend into the high temperature foam, embedded between the foam insulation and HDPE jacket.  The longitudinal length of the water stop will be determined by the manufacturer based on project design conditions to sufficiently dissipate the heat from the carrier pipe protecting the integrity of the high temperature insulation.  The water stop shall have been manufacturer tested and proved to contain for a minimum of 12 months the spread of groundwater through the system that is capable of flashing to steam when in contact with the hot carrier pipe.  This spread of moisture shall be contained in the immediate area of a field joint and not allowed to spread further.  Testing data and results shall be provided by the Manufacturer that the Manufacturer’s water stop limiting device is capable of isolating water spread to within 5” of the joint area on a pipe operating in excess of 300F, with a column of water exposed and boiling in the joint area for the entire 6 month period.

2.4	Jacketing material shall be extruded, black, high density polyethylene (HDPE), having a minimum wall thickness of 125 mils. for jacket sizes less than or equal to 12”, 150 mils. For jacket sizes greater than 12” to 20”, and 175 mils. For jacket sizes larger than 20”.  The jacket throughout the entire system shall incorporate electric fusion, butt fusion, or extrusion welding at all HDPE fittings, joint closures, or other points of connection.  This shall create a jacket that is seamless throughout the entire system with the exception of anchors, whose water shed rings are sealed with a double wrap heat shrink materials prohibiting the ingression of water.  The inner surface of the HDPE jacket shall be oxidized by means of corona treatment or other approved methods to create a secure bond to the foam.

2.5	Straight run joints are insulated using a high temperature foam to the thickness specified and jacketed with an electric fusion pressure testable joint closure.  The joint closure will be fused to the adjacent jacket material creating a weld as strong as or stronger than the jacket.  Shrink materials and adhesives shall not be allowed as primary sealing means.  The joint will be pressure tested at 5 psi for 5 minutes while simultaneously soap tested at the joint closure’s seams for possible leaks.  After passing the pressure test, the field joint is insulated and closure patches are welded (as per specified joint closure instructions) over the foaming holes.  All joint closures and insulation shall occur at straight sections of pipe.  A log will be made showing who made the joint, the amount of time for the fusion, and that the joint was inspected.  This is a permanent record and will be furnished as a close-out document. No warranty shall be issued until the pressure testable joint closure log is completed and returned to the manufacturer.

2.6	Terminations inside of manholes shall have a corrosion coated steel sleeve protecting the foam.  This steel sleeve shall be fillet welded onto the carrier pipe and come up and extend back on the jacket a distance of 16”.  A high temperature shrink sleeve 4” wide shall be used to seal the steel sleeve to the HDPE jacket.

2.7	Fittings are factory pre-fabricated and pre-insulated with polyisocyanurate to the thickness specified and jacketed with a one piece seamless molded HDPE fitting cover, a butt fusion welded, or an extrusion welded and mitered HDPE jacket.  No taping shall be allowed as primary sealing method.  All fitting jackets/covers shall be connected to the straight lengths of pipe by electro fusion, butt fusion, or extrusion welding.  Carrier pipe fittings shall be butt-welded, except for sizes smaller than 2”, which shall be socket-welded.  Fittings include expansion loops, elbows, tees, reducers, and anchors.  Elbows, loops, offsets, or any other direction changes shall conform to the standards set by ANSI B31.1, Code for Power Piping.

2.8     Anchors shall be designed as thermally isolated so that any portion of exposed plate does not exceed 200F.  The metal anchor shall be welded to a standard weight casing that is extended in parallel into the high temperature foam insulation, before turning down and fully welded to the carrier pipe.  The anchor casing shall be insulated between the carrier pipe and the HDPE jacket. The overall length of the anchor casing, along with the insulation requirements shall be determined by the manufacturer who shall submit a finite element heat analysis showing profile of the pipe and anchor heat distribution with a maximum exposed anchor plate temperature of not more than 200F.  The finite element analysis shall be representative of the pipe size and operating temperature specified.  Anchors shall be ½” thick steel plates and shall incorporate a steel water shed ring sealed to the HDPE jacket with a heat shrink wrap.  Anchors are located per manufacturer’s recommendations.

2.9	Expansion/contraction compensation will be accomplished utilizing factory pre-fabricated and pre-insulated expansion elbows, Z-bends, expansion loops, and anchors specifically designed for the intended application. Flexible expansion pads shall be utilized for external expansion compensation on all fittings having expansion in excess of 1/2".  Expansion pads shall be a minimum one inch thick and shall extend to cover both the inside and outside radius of the fittings.

2.10    Electric Resistance Monitoring shall be provided to leak detect the entire system.  The ERM system consists of a copper wire embedded in the foam of each piece of pre-insulated pipe and fittings.  The piping system manufacturer shall install the wire in a manner that prevents touching the steel carrier pipe.  The contractor shall connect the wire together at each field joint with a recommended crimping tool.  After crimping the wire at a joint, the contractor shall check the jointed pieces for continuity of the wire and electrical isolation from the carrier pipe by use of a standard analog ohmmeter.  This check shall be repeated after each crimp, until the entire system is connected.  After the piping system is installed, the owner at any time may check the system for a leak by using a standard analog ohmmeter.  If a leak is detected (a leak is signaled by a drastic drop in the electrical resistance of the circuit), the panel will alarm, and the owner should contact the system manufacturer for TDR instrument to determine the location of the leak.  One or more alarm panels are furnished with each ERM system, designed to monitor up to 2000’, which will provide continuous leak detection monitoring.

Part 3 – Execution

3.1	Pre-engineered systems shall be provided with all straight pipe and fittings factory pre-insulated and pre-fabricated to job dimensions.

3.2	Underground systems shall be buried in a trench not less than two feet deeper than the top of the pipe and not less than eighteen inches wider than the combined O.D. of all piping systems.  A minimum thickness of 24 inches of compacted backfill placed over the top of the pipe will meet H-20 highway loading.

3.3	Trench bottom shall have a minimum of 6” of sand, or manufacturer’s approved backfill.  All field-cutting of the pipe shall be performed in accordance with the manufacturer’s installation instructions.

3.4	A hydrostatic pressure test of the carrier pipe shall be performed per the engineer’s specification with a factory recommendation of one and one-half times the normal system operating pressure for not less than two hours.  Care shall be taken to insure all trapped air is removed from the system prior to the test.  Appropriate safety precautions shall be taken to guard against possible injury to personnel in the event of a failure.

3.5	Field Service is required and will be provided by a certified manufacturer’s representative or company field service technician.  The technician will be available at the job as required to ensure the contractor understands and has interpreted the installation instructions with respect to unloading, storing and handling of pipe, pipe installation, pressure testing, field joint insulation, leak detection connection, and backfilling techniques.

3.6	A Final ERM Panel Test is required with the owner’s representative present, along with the contractor and the Thermacor Field service representative. No warranty shall be issued until the ERM log sheets are completed and returned to the manufacturer.

# Text boxes

## THERMACOR

### HT-406

#### Specification Guide

STANDARD SPECIFICATION

#### HTSG

2.101

11.14.11